Firmware Revision Information

Product Code(s): ACR1000A-CTL-(24-ULT)

Product Name(s): iPath System Manager

Date Modified: June 30th, 2017

# Special Release Only

# Scope:

This is a hot fix to resolve a field reported issue of the Backup iPath not updating the primary iPath connection log correctly when the primary iPath comes back online.

# Version 4.6.40294

Fixes:

-  On recovery from a failover changes made by the acting primary are not always written back to the primary when it comes back online.

-  The device Daemon misreports devices as offline after a failover

- It is not possible to create a channel with the same video source for both video heads.

Known Issues:

-  When performing an upgrade you need to ensure that there is sufficient free space on the backup partition for the backup to be made during the upgrade process.  You can delete backups or firmware upgrade files from this partition.  Ensure that the connection and event logs are archived regularly to prevent these files from becoming too large.