Model  IC832A & IC833A

USB to RS-485 Mini-Converter

Features

- Connects an RS-485 2-Wire or 4-Wire device to your USB Port

- Terminal Block for RS-485 Connection

- USB Port Powered

- USB 2.0 Compatible

- RS-485 Data Rates up to 921.6 kbps

- Automatic Configuration on Windows 2000, XP, Vista & Windows 7

- High Retention USB Connector

Functional Description

Universal Serial Bus (USB) has become the connectivity workhorse of today’s PCs, replacing the familiar serial ports. However, many commercial and industrial devices still use the RS-485 interface. To connect these devices to modern PCs, you need a simple and reliable conversion solution. The IC832A and IC833A offer this solution in a space saving, USB Port powered package. Simply plug the converter into an available USB port on your computer or USB hub and install the drivers supplied on CD ROM. The device will show up as an additional COM port in the Windows Device Manager which is fully compatible with your Windows applications. A one-meter USB cable is included.

Operation

- Drivers are included on the Compact Disk included with the converter. Simply connect the converter to an available USB port and insert the CD into the drive. The “Found New Hardware Wizard” will guide you through the installation process. The drivers are not available via Microsoft Windows Updates. When prompted to connect to Windows Updates to search for drivers, select “No, not at this time” and follow the instructions for installing from the CD.

- When the driver software is installed, the converter will show up in Windows Device Manager as the next available COM port labeled “RS-485 Port.”  Configure the COM port for your application. The default setup is 9600 baud, 8 data bits, no parity, 1 stop bit, no flow control. The converter will also be listed under USB Controllers.

- To uninstall the drivers, follow the instructions contained in the uninstall “read me” file.

- Use the IC832A for RS-485 2-Wire systems. In the 2-Wire configuration, the receiver toggles with the transmit data. Bias is provided by 4.7 KΩ pull-up and pull-down resistors.

- Use the IC833A for RS-485 4-Wire systems. In the 4-Wire configuration, the receiver is always active. Bias is provided by 4.7 KΩ pull-up and pull-down resistors on the receive pair. Bias should be provided on the transmit pair by the end of line slave device.

- In most applications, termination is not required. If your application does require termination, it must be installed external to the converter.

Ordering Information

| Model Number | Description |
| --- | --- |
| IC832A | USB to RS-485 2-Wire Converter with Terminal Block |
| IC833A | USB to RS-485 4-Wire Converter with Terminal Block |

| Table 1 |  |  |  | General Specifications |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| IC832A Terminal Block Layout |  |  |  |  |  |  |  |  |
| Label | Use |  |  |  | Input Power | 5VDC from USB Port |  |  |
| A(-) | Data A (-) |  |  |  | Current Draw | Low Power Device (<100 mA) |  |  |
| B(+) | Data B (+) |  |  |  | Operating Temperature | -40 to 176 °F (-40 to 80 °C) |  |  |
| A(-) | Data A (-) |  |  |  | Operating Humidity | 0 to 95% Non-condensing |  |  |
| B(+) | Data B (+) |  |  |  | USB Connector | USB type B Female |  |  |
| GND | Ground |  |  |  | RS-485 Connector | Terminal Block |  |  |
|  |  |  |  |  | USB Data Rate | 12 Mbps |  |  |
|  |  |  |  |  | RS-485 Data Rate | 921.6 kbps |  |  |
| Table 2 |  |  |  |  | USB Standard | 2.0 (Backward Compatible) |  |  |
| IC833A Terminal Block Layout |  |  |  |  | Dimensions | 2.6 x 1.3 x .6 in (6.5 x 3.2 x 1.6 cm) |  |  |
| Label | Use |  |  |  | MTBF (IC832A) | 2130833 hours |  |  |
| TDA(-) | Transmit Data A (-) |  |  |  | MTBF (IC833A) | 1869313 hours |  |  |
| TDB(+) | Transmit Data B (+) |  |  |  | Approvals | CE, FCC |  |  |
| RDA(-) | Receive Data A (-) |  |  |  |  |  |  |  |
| RDB(+) | Receive Data B (+) |  |  |  |  |  |  |  |
| GND | Ground |  |  |  |  |  |  |  |

IC832A Wiring

- This converter is used for RS-485 2-Wire Systems.

- Loosen the screws to open the Terminal Block lead clamps for the A(-), B(+), and GND terminals.

- Insert the RS-485 2-Wire signal leads in accordance with the diagram above. The TB will accept 28 to 16 AWG wire.

- Tighten the screws to close the TB lead clamps. Ensure the clamps hold the leads securely. However, do not over tighten.

- Bias is provided by 4.7KΩ pull-up and pull-down resistors.

- If termination is required, it must be installed externally. In most cases, termination is not required.

- During operation, the receiver toggles with the transmit data.

- Please contact Black Box Tech support for application notes regarding termination and biasing.

| Model Number: | IC832A and IC833A |  |
| --- | --- | --- |
| Description: | USB to RS-485 Converter |  |
| Type: | Light Industrial ITE Equipment |  |
| Application of Council Directive: | 89/336/EEC |  |
| Standards: | EN55022 |  |
|  | EN 61000-6-1 |  |
|  | EN 61000 (-4-2, -4-3, -4-4, -4-5, -4-6, -4-8, -4-11) |  |

CE Declaration of Conformity

IC833A Wiring

- This converter is used for RS-485 4-Wire Systems.

- Loosen the screws to open the Terminal Block lead clamps for the TDA(-), TDB(+), RDA(-), RDB(+), and GND terminals.

- Insert the RS-485 2-Wire signal leads in accordance with the diagram above. The TB will accept 28 to 16 AWG wire.

- Tighten the screws to close the TB lead clamps. Ensure the clamps hold the leads securely. However, do not over tighten.

- Bias is provided by 4.7KΩ pull-up and pull-down resistors.

- If termination is required, it must be installed externally. In most cases, termination is not required.

- During operation, the receiver is always active.

- Please contact Black Box Tech support for application notes regarding termination and biasing.

IC833A Loop Back Test

- Loopback TDA(-) to RDA(-) and TDB(+) to RDB(+) as shown in the diagram above.

- Using Hyper Terminal or similar program, connect to the appropriate COM port. Set the desired baud rate. Ensure Hyper Terminal local echo is OFF.

- Transmit data. If the same character string is returned, the test is good.

- Please contact Black Box Tech Support for additional help with this test.

IC832A Back to Back Test

- Due to the circuit configuration, a loop back test is not possible with this model. However, two converters can be used in a back to back configuration.

- Wire the converters as shown above.

- Using Hyper Terminal or similar program, connect to the appropriate COM ports. Set the desired baud rate.

- Transmit data. If the same string is received on the distant end, the test is good.